## control_config
parameter | value
VOLTAGE_MIN_PU | 0.9
TARGET_VOLTAGE_PU | 1
VOLTAGE_MAX_PU | 1.1
U_MIN_ALLOWED_OBJ | 0.95
U_MAX_ALLOWED_OBJ | 1.05
LOADING_MAX_PERCENT | 100
P_STORAGE_TOTAL_MAX_KW | 90
P_STORAGE_PHASE_MAX_KW | 30
ALLOW_STORAGE_CHARGE | TRUE
ALLOW_STORAGE_DISCHARGE | TRUE
KEEP_INITIAL_STORAGE_Q | TRUE
NONCONVERGENCE_PENALTY | 1000000
PSO_N_PARTICLES | 3
PSO_N_ITER | 3
W_CRIT_U | 0.3
W_CRIT_VU | 0.25
W_CRIT_L | 0.3
W_CRIT_PEN | 0.1
W_CRIT_CTRL | 0.05
W_TRAFO_EXP | 0.3
W_TRAFO_I | 0.2
W_TRAFO_IMP | 0.1
W_TRAFO_ULIM | 0.15
W_TRAFO_L | 0.15
W_TRAFO_CTRL | 0.1
PSO_W | 0.7
PSO_C1 | 1.5
PSO_C2 | 1.5
PSO_RANDOM_SEED | 42

## loads_input
name | type | P1_kW | P2_kW | P3_kW | Q1_kvar | Q2_kvar | Q3_kvar
LD10 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD102 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD103 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD104 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD106 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD107 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD11 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD110 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD112 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD113 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD114 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD115 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD116 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD12 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD13 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD21 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD25 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD26 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD29 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD30 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD33 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD34 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD37 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD39 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD40 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD42 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD45 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD46 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD47 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD49 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD5 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD50 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD52 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD54 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD57 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD60 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD62 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD64 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD66 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD67 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD7 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD72 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD73 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD75 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD76 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD77 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD80 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD81 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD83 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD87 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD88 | load | 0 | 1 | 0 | 0 | 0.32868 | 0
LD93 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD95 | load | 1 | 0 | 0 | 0.32868 | 0 | 0
LD96 | load | 0.8 | 0.8 | 0.8 | 0.26295 | 0.26295 | 0.26295
LD97 | load | 1 | 0 | 0 | 0.32868 | 0 | 0

## pv_input
name | type | P_kW | Q_kvar | Smax_kVA | control_mode
PV102F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV102F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV102F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV103F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV103F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV103F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV104F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV104F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV104F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV106F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV106F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV106F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV107F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV107F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV107F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV10F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV10F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV10F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV110F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV110F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV110F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV112F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV112F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV112F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV113F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV113F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV113F3 | pv | 2 | 0 | 0 | to_be_set_qvchar
PV114F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV114F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV114F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV115F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV115F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV115F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV116F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV116F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV116F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV11F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV11F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV11F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV12F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV12F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV12F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV13F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV13F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV13F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV21F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV21F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV21F3 | pv | 2 | 0 | 0 | to_be_set_qvchar
PV25F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV25F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV25F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV26F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV26F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV26F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV29F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV29F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV29F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV30F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV30F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV30F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV33F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV33F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV33F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV34F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV34F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV34F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV37F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV37F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV37F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV39F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV39F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV39F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV40F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV40F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV40F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV42F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV42F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV42F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV45F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV45F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV45F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV46F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV46F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV46F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV47F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV47F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV47F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV49F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV49F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV49F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV50F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV50F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV50F3 | pv | 2 | 0 | 0 | to_be_set_qvchar
PV52F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV52F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV52F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV54F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV54F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV54F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV57F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV57F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV57F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV5F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV5F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV5F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV60F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV60F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV60F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV62F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV62F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV62F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV64F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV64F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV64F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV66F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV66F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV66F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV67F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV67F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV67F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV72F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV72F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV72F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV73F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV73F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV73F3 | pv | 2 | 0 | 0 | to_be_set_qvchar
PV75F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV75F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV75F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV76F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV76F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV76F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV77F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV77F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV77F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV7F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV7F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV7F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV80F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV80F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV80F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV81F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV81F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV81F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV83F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV83F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV83F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV87F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV87F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV87F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV88F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV88F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV88F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV93F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV93F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV93F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV95F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV95F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV95F3 | pv | 2 | 0 | 0 | to_be_set_qvchar
PV96F1 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV96F2 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV96F3 | pv | 0 | 0 | 0 | to_be_set_qvchar
PV97F1 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV97F2 | pv | 1.76 | 0 | 0 | to_be_set_qvchar
PV97F3 | pv | 1.76 | 0 | 0 | to_be_set_qvchar

## other_generators_input
name | type | P_kW | Q_kvar
ES100F1 | StatGen | 0 | 0
ES100F2 | StatGen | 0 | 0
ES100F3 | StatGen | 0 | 0
ES101F1 | StatGen | 0 | 0
ES101F2 | StatGen | 0 | 0
ES101F3 | StatGen | 0 | 0
ES110F1 | StatGen | 0 | 0
ES110F2 | StatGen | 0 | 0
ES110F3 | StatGen | 0 | 0
ES14F1 | StatGen | 0 | 0
ES14F2 | StatGen | 0 | 0
ES14F3 | StatGen | 0 | 0
ES15F1 | StatGen | 0 | 0
ES15F2 | StatGen | 0 | 0
ES15F3 | StatGen | 0 | 0
ES28F1 | StatGen | 0 | 0
ES28F2 | StatGen | 0 | 0
ES28F3 | StatGen | 0 | 0
ES29F1 | StatGen | 0 | 0
ES29F2 | StatGen | 0 | 0
ES29F3 | StatGen | 0 | 0
ES2F1 | StatGen | 0 | 0
ES2F2 | StatGen | 0 | 0
ES2F3 | StatGen | 0 | 0
ES32F1 | StatGen | 0 | 0
ES32F2 | StatGen | 0 | 0
ES32F3 | StatGen | 0 | 0
ES35F1 | StatGen | 0 | 0
ES35F2 | StatGen | 0 | 0
ES35F3 | StatGen | 0 | 0
ES38F1 | StatGen | 0 | 0
ES38F2 | StatGen | 0 | 0
ES38F3 | StatGen | 0 | 0
ES39F1 | StatGen | 0 | 0
ES39F2 | StatGen | 0 | 0
ES39F3 | StatGen | 0 | 0
ES40F1 | StatGen | 0 | 0
ES40F2 | StatGen | 0 | 0
ES40F3 | StatGen | 0 | 0
ES41F1 | StatGen | 0 | 0
ES41F2 | StatGen | 0 | 0
ES41F3 | StatGen | 0 | 0
ES43F1 | StatGen | 0 | 0
ES43F2 | StatGen | 0 | 0
ES43F3 | StatGen | 0 | 0
ES48F1 | StatGen | 0 | 0
ES48F2 | StatGen | 0 | 0
ES48F3 | StatGen | 0 | 0
ES4F1 | StatGen | 0 | 0
ES4F2 | StatGen | 0 | 0
ES4F3 | StatGen | 0 | 0
ES50F1 | StatGen | 0 | 0
ES50F2 | StatGen | 0 | 0
ES50F3 | StatGen | 0 | 0
ES51F1 | StatGen | 0 | 0
ES51F2 | StatGen | 0 | 0
ES51F3 | StatGen | 0 | 0
ES53F1 | StatGen | 0 | 0
ES53F2 | StatGen | 0 | 0
ES53F3 | StatGen | 0 | 0
ES54F1 | StatGen | 0 | 0
ES54F2 | StatGen | 0 | 0
ES54F3 | StatGen | 0 | 0
ES55F1 | StatGen | 0 | 0
ES55F2 | StatGen | 0 | 0
ES55F3 | StatGen | 0 | 0
ES58F1 | StatGen | 0 | 0
ES58F2 | StatGen | 0 | 0
ES58F3 | StatGen | 0 | 0
ES59F1 | StatGen | 0 | 0
ES59F2 | StatGen | 0 | 0
ES59F3 | StatGen | 0 | 0
ES65F1 | StatGen | 0 | 0
ES65F2 | StatGen | 0 | 0
ES65F3 | StatGen | 0 | 0
ES66F1 | StatGen | 0 | 0
ES66F2 | StatGen | 0 | 0
ES66F3 | StatGen | 0 | 0
ES68F1 | StatGen | 0 | 0
ES68F2 | StatGen | 0 | 0
ES68F3 | StatGen | 0 | 0
ES69F1 | StatGen | 0 | 0
ES69F2 | StatGen | 0 | 0
ES69F3 | StatGen | 0 | 0
ES70F1 | StatGen | 0 | 0
ES70F2 | StatGen | 0 | 0
ES70F3 | StatGen | 0 | 0
ES71F1 | StatGen | 0 | 0
ES71F2 | StatGen | 0 | 0
ES71F3 | StatGen | 0 | 0
ES74F1 | StatGen | 0 | 0
ES74F2 | StatGen | 0 | 0
ES74F3 | StatGen | 0 | 0
ES79F1 | StatGen | 0 | 0
ES79F2 | StatGen | 0 | 0
ES79F3 | StatGen | 0 | 0
ES80F1 | StatGen | 0 | 0
ES80F2 | StatGen | 0 | 0
ES80F3 | StatGen | 0 | 0
ES82F1 | StatGen | 0 | 0
ES82F2 | StatGen | 0 | 0
ES82F3 | StatGen | 0 | 0
ES85F1 | StatGen | 0 | 0
ES85F2 | StatGen | 0 | 0
ES85F3 | StatGen | 0 | 0
ES86F1 | StatGen | 0 | 0
ES86F2 | StatGen | 0 | 0
ES86F3 | StatGen | 0 | 0
ES89F1 | StatGen | 0 | 0
ES89F2 | StatGen | 0 | 0
ES89F3 | StatGen | 0 | 0
ES8F1 | StatGen | 0 | 0
ES8F2 | StatGen | 0 | 0
ES8F3 | StatGen | 0 | 0
ES90F1 | StatGen | 0 | 0
ES90F2 | StatGen | 0 | 0
ES90F3 | StatGen | 0 | 0
ES92F1 | StatGen | 0 | 0
ES92F2 | StatGen | 0 | 0
ES92F3 | StatGen | 0 | 0
ES99F1 | StatGen | 0 | 0
ES99F2 | StatGen | 0 | 0
ES99F3 | StatGen | 0 | 0

## critical_storage_meta
node | role | elem_L1 | elem_L2 | elem_L3 | Pmax_kW | Smax_kVA
101 | critical | ES101F1 | ES101F2 | ES101F3 | 30 | 35

## storage_steps_from_excel
step | P_pu
-10 | -1
-9 | -0.9
-8 | -0.8
-7 | -0.7
-6 | -0.6
-5 | -0.5
-4 | -0.4
-3 | -0.3
-2 | -0.2
-1 | -0.1
0 | 0
1 | 0.1
2 | 0.2
3 | 0.3
4 | 0.4
5 | 0.5
6 | 0.6
7 | 0.7
8 | 0.8
9 | 0.9
10 | 1

## storage_input
node | element | phase | step_label | step_pu | search_direction | u_before_pu | u_after_pu | voltage_error_abs | p_storage_kw | q_storage_kvar | Pmax_kW | Smax_kVA | p_storage_kw_in_model | q_storage_kvar_in_model
101 | ES101F1 | L1 | 3 | 0.3 | start | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | -9 | 0
101 | ES101F2 | L2 | 1 | 0.1 | start | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | -3 | 0
101 | ES101F3 | L3 | 4 | 0.4 | start | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | -12 | 0

## node_voltages
node | U_L1_pu | angle_L1_deg | U_L2_pu | angle_L2_deg | U_L3_pu | angle_L3_deg | kU2_percent
0 | 1.05 | 7.4051e-05 | 1.05 | -120.0001 | 1.05 | 120 | 0.00018892
1 | 1.0421 | -149.6865 | 1.0359 | 90.3429 | 1.0382 | -29.3735 | 0.34471
10 | 1.0424 | -148.9043 | 1.0319 | 91.5658 | 1.0424 | -28.0814 | 0.75274
100 | 0.99887 | -146.9416 | 0.99412 | 95.7872 | 1.005 | -24.6347 | 1.7988
101 | 0.99453 | -147.0045 | 0.99224 | 95.7778 | 0.99954 | -24.7427 | 1.7109
102 | 1.0119 | -146.747 | 1.0014 | 95.8069 | 1.0204 | -24.3702 | 1.9794
103 | 1.0287 | -146.6283 | 1.0126 | 95.4564 | 1.0399 | -24.2118 | 2.0923
104 | 1.0089 | -146.8146 | 0.99917 | 95.8175 | 1.0166 | -24.4251 | 1.9631
105 | 1.0283 | -146.6469 | 1.0121 | 95.45 | 1.0395 | -24.2258 | 2.0996
106 | 1.0282 | -146.6542 | 1.0117 | 95.4579 | 1.0394 | -24.2184 | 2.1173
107 | 1.0288 | -146.6226 | 1.0126 | 95.4615 | 1.0399 | -24.2033 | 2.0948
108 | 0.99437 | -147.0028 | 0.99206 | 95.7819 | 0.9994 | -24.7479 | 1.7119
109 | 1.0031 | -146.8803 | 0.99576 | 95.7981 | 1.0107 | -24.5236 | 1.9027
11 | 1.0422 | -148.4015 | 1.0286 | 92.4039 | 1.0454 | -27.1985 | 1.1125
110 | 0.99412 | -146.9954 | 0.99195 | 95.7963 | 0.99925 | -24.761 | 1.7105
111 | 1.0165 | -146.7138 | 1.0042 | 95.7556 | 1.0253 | -24.2683 | 2.0314
112 | 1.0171 | -146.7046 | 1.0047 | 95.768 | 1.0258 | -24.2467 | 2.0356
113 | 1.0031 | -146.8864 | 0.99535 | 95.8073 | 1.0116 | -24.5155 | 1.951
114 | 0.99405 | -146.9947 | 0.99157 | 95.7932 | 0.99896 | -24.747 | 1.7126
115 | 1.0174 | -146.7178 | 1.0047 | 95.7668 | 1.0261 | -24.2436 | 2.0525
116 | 1.0028 | -146.8728 | 0.99528 | 95.8087 | 1.0102 | -24.5218 | 1.9034
12 | 1.0419 | -148.3888 | 1.0286 | 92.4049 | 1.045 | -27.2016 | 1.0958
13 | 1.0435 | -148.5374 | 1.0315 | 92.1321 | 1.0455 | -27.5039 | 0.94806
14 | 1.0426 | -148.0847 | 1.0279 | 92.8899 | 1.0477 | -26.6942 | 1.2896
15 | 1.0425 | -147.8059 | 1.0268 | 93.3255 | 1.0488 | -26.2608 | 1.435
16 | 1.0425 | -147.7888 | 1.0268 | 93.3506 | 1.0488 | -26.2418 | 1.4391
17 | 1.0423 | -147.7815 | 1.0266 | 93.3651 | 1.0487 | -26.2326 | 1.4434
18 | 1.0424 | -147.7744 | 1.0266 | 93.3761 | 1.0488 | -26.2203 | 1.4489
19 | 1.0426 | -148.0734 | 1.0277 | 92.9151 | 1.048 | -26.6585 | 1.3156
2 | 1.0427 | -148.921 | 1.0323 | 91.5435 | 1.0427 | -28.1062 | 0.74393
20 | 1.0428 | -148.062 | 1.0277 | 92.9399 | 1.0483 | -26.6339 | 1.3306
21 | 1.0422 | -148.068 | 1.0273 | 92.9221 | 1.0486 | -26.6322 | 1.346
22 | 1.0429 | -148.0549 | 1.0278 | 92.9536 | 1.0484 | -26.6243 | 1.3343
23 | 1.0429 | -148.0578 | 1.0276 | 92.9511 | 1.0483 | -26.6188 | 1.3418
24 | 1.0428 | -148.0635 | 1.0273 | 92.9518 | 1.0482 | -26.6135 | 1.3531
25 | 1.0428 | -148.062 | 1.0275 | 92.9595 | 1.0484 | -26.6155 | 1.3515
26 | 1.0433 | -148.0342 | 1.028 | 92.9768 | 1.0487 | -26.5951 | 1.3413
27 | 1.0428 | -148.0692 | 1.0271 | 92.9524 | 1.0482 | -26.6083 | 1.3644
28 | 1.0426 | -147.5669 | 1.026 | 93.7038 | 1.05 | -25.8721 | 1.5715
29 | 1.0426 | -148.0763 | 1.0268 | 92.9583 | 1.0481 | -26.5994 | 1.3816
3 | 1.0428 | -148.9102 | 1.0323 | 91.5593 | 1.0428 | -28.0872 | 0.75245
30 | 1.0426 | -148.0763 | 1.0268 | 92.9583 | 1.0481 | -26.5994 | 1.3816
31 | 1.0421 | -147.7814 | 1.0264 | 93.3686 | 1.0485 | -26.2356 | 1.4421
32 | 1.0423 | -147.351 | 1.0247 | 94.0516 | 1.0507 | -25.4999 | 1.712
33 | 1.0434 | -148.032 | 1.0286 | 92.9823 | 1.0492 | -26.6135 | 1.3248
34 | 1.0417 | -147.7765 | 1.0264 | 93.3789 | 1.0484 | -26.2428 | 1.434
35 | 1.0418 | -147.1579 | 1.0231 | 94.3775 | 1.0512 | -25.1504 | 1.8537
36 | 1.0425 | -147.7673 | 1.0266 | 93.3871 | 1.0488 | -26.2079 | 1.4544
37 | 1.0429 | -147.7651 | 1.0272 | 93.3764 | 1.0492 | -26.2183 | 1.4386
38 | 1.0424 | -147.0737 | 1.0225 | 94.5288 | 1.0526 | -24.979 | 1.9557
39 | 1.0417 | -147.7758 | 1.026 | 93.3758 | 1.0481 | -26.23 | 1.4427
4 | 1.0428 | -148.5763 | 1.0308 | 92.0892 | 1.0448 | -27.5403 | 0.95015
40 | 1.0432 | -147.7563 | 1.0271 | 93.4118 | 1.0496 | -26.1814 | 1.4705
41 | 1.0433 | -146.982 | 1.0225 | 94.6775 | 1.0537 | -24.842 | 2.015
42 | 1.0421 | -147.7617 | 1.0262 | 93.3942 | 1.0484 | -26.2023 | 1.455
43 | 1.0444 | -146.8832 | 1.0229 | 94.8249 | 1.0549 | -24.7117 | 2.06
44 | 1.0422 | -147.0767 | 1.0222 | 94.5298 | 1.0527 | -24.9655 | 1.9725
45 | 1.0433 | -146.9848 | 1.0224 | 94.6779 | 1.0537 | -24.8396 | 2.0206
46 | 1.0425 | -147.3361 | 1.0249 | 94.0665 | 1.0509 | -25.4854 | 1.7114
47 | 1.0421 | -147.0841 | 1.0219 | 94.5364 | 1.0526 | -24.957 | 1.9899
48 | 1.0407 | -147.0416 | 1.0222 | 94.5658 | 1.0505 | -24.9578 | 1.9022
49 | 1.0428 | -147.5509 | 1.0264 | 93.7253 | 1.0503 | -25.8613 | 1.5688
5 | 1.0443 | -148.8876 | 1.0334 | 91.6072 | 1.0444 | -28.0332 | 0.78447
50 | 1.0418 | -147.0716 | 1.0218 | 94.5375 | 1.0532 | -24.9397 | 2.0038
51 | 1.0394 | -146.9481 | 1.021 | 94.7367 | 1.0496 | -24.787 | 1.9538
52 | 1.0443 | -146.886 | 1.0227 | 94.8254 | 1.0548 | -24.7092 | 2.0656
53 | 1.0455 | -146.7776 | 1.0235 | 94.9711 | 1.0562 | -24.5878 | 2.0908
54 | 1.0408 | -147.0342 | 1.0223 | 94.5716 | 1.0506 | -24.9506 | 1.9012
55 | 1.046 | -146.69 | 1.0239 | 95.0949 | 1.0569 | -24.4949 | 2.1104
56 | 1.0457 | -146.6898 | 1.0237 | 95.0986 | 1.0567 | -24.4982 | 2.1096
57 | 1.0453 | -146.6843 | 1.0233 | 95.1061 | 1.0563 | -24.4929 | 2.1105
58 | 1.0376 | -146.8642 | 1.0197 | 94.8902 | 1.0483 | -24.6496 | 1.984
59 | 1.0471 | -146.6032 | 1.0246 | 95.2093 | 1.0581 | -24.394 | 2.1322
6 | 1.043 | -148.5613 | 1.0311 | 92.1069 | 1.0451 | -27.5277 | 0.94837
60 | 1.0381 | -146.8407 | 1.0202 | 94.9014 | 1.0487 | -24.6266 | 1.9799
61 | 1.0398 | -146.9406 | 1.021 | 94.75 | 1.05 | -24.7616 | 1.9703
62 | 1.0406 | -146.9298 | 1.0216 | 94.7639 | 1.0507 | -24.7355 | 1.9838
63 | 1.0474 | -146.5862 | 1.0249 | 95.2299 | 1.0584 | -24.3725 | 2.1368
64 | 1.0397 | -146.948 | 1.0207 | 94.757 | 1.0499 | -24.7534 | 1.9877
65 | 1.0474 | -146.5594 | 1.0248 | 95.2713 | 1.0584 | -24.3478 | 2.1422
66 | 1.0482 | -146.5752 | 1.0254 | 95.2538 | 1.0592 | -24.3468 | 2.1522
67 | 1.0454 | -146.6849 | 1.0236 | 95.1091 | 1.0566 | -24.5056 | 2.1025
68 | 1.0353 | -146.7974 | 1.018 | 95.0435 | 1.0466 | -24.5229 | 2.0228
69 | 1.0467 | -146.5587 | 1.0243 | 95.2805 | 1.058 | -24.356 | 2.1403
7 | 1.0441 | -148.5121 | 1.0328 | 92.1674 | 1.0466 | -27.5042 | 0.92632
70 | 1.0465 | -146.5582 | 1.0243 | 95.2886 | 1.0579 | -24.3637 | 2.1377
71 | 1.0327 | -146.7562 | 1.0156 | 95.1756 | 1.0444 | -24.4123 | 2.0709
72 | 1.0479 | -146.5627 | 1.0253 | 95.2547 | 1.0588 | -24.3497 | 2.1358
73 | 1.0326 | -146.7562 | 1.0155 | 95.1762 | 1.0445 | -24.4042 | 2.0795
74 | 1.0303 | -146.7147 | 1.0136 | 95.3061 | 1.0418 | -24.3286 | 2.0905
75 | 1.0466 | -146.5587 | 1.0242 | 95.281 | 1.0579 | -24.3562 | 2.1406
76 | 1.0457 | -146.7705 | 1.0237 | 94.9799 | 1.0564 | -24.5757 | 2.0952
77 | 1.0464 | -146.558 | 1.0242 | 95.2918 | 1.0579 | -24.3668 | 2.1368
78 | 1.0477 | -146.5424 | 1.025 | 95.2922 | 1.0588 | -24.3263 | 2.1469
79 | 1.028 | -146.666 | 1.012 | 95.4353 | 1.0393 | -24.2499 | 2.0964
8 | 1.0426 | -148.3897 | 1.0295 | 92.3971 | 1.0457 | -27.212 | 1.0852
80 | 1.0482 | -146.5189 | 1.0255 | 95.3175 | 1.0592 | -24.3035 | 2.146
81 | 1.0484 | -146.5314 | 1.0256 | 95.3166 | 1.0595 | -24.3005 | 2.1624
82 | 1.0251 | -146.6626 | 1.01 | 95.5323 | 1.0364 | -24.2236 | 2.1005
83 | 1.0303 | -146.7168 | 1.0135 | 95.3067 | 1.0418 | -24.327 | 2.0947
84 | 1.0251 | -146.6547 | 1.0101 | 95.5397 | 1.0366 | -24.2108 | 2.1069
85 | 1.0221 | -146.686 | 1.0078 | 95.6048 | 1.0326 | -24.2404 | 2.0841
86 | 1.0192 | -146.703 | 1.0059 | 95.6754 | 1.0288 | -24.2622 | 2.0548
87 | 1.0256 | -146.6307 | 1.0105 | 95.5514 | 1.0371 | -24.1885 | 2.1021
88 | 1.0221 | -146.6879 | 1.0077 | 95.6054 | 1.0325 | -24.239 | 2.0883
89 | 1.0162 | -146.72 | 1.004 | 95.7463 | 1.0251 | -24.284 | 2.0265
9 | 1.0423 | -148.3946 | 1.029 | 92.3981 | 1.0454 | -27.2074 | 1.0954
90 | 1.0121 | -146.7584 | 1.0015 | 95.7861 | 1.0205 | -24.3595 | 1.9835
91 | 1.0122 | -146.7535 | 1.0015 | 95.7937 | 1.0206 | -24.3592 | 1.9836
92 | 1.0079 | -146.8139 | 0.99869 | 95.8005 | 1.0157 | -24.4368 | 1.9425
93 | 1.0127 | -146.744 | 1.0019 | 95.8063 | 1.021 | -24.3514 | 1.9842
94 | 1.008 | -146.8111 | 0.99868 | 95.8059 | 1.0157 | -24.4329 | 1.9464
95 | 1.0248 | -146.6496 | 1.01 | 95.552 | 1.0375 | -24.199 | 2.1335
96 | 1.0077 | -146.8038 | 0.9982 | 95.8162 | 1.0153 | -24.4307 | 1.9472
97 | 1.0354 | -146.7898 | 1.0182 | 95.0499 | 1.0468 | -24.518 | 2.0203
98 | 1.0282 | -146.6526 | 1.0121 | 95.4449 | 1.0394 | -24.2343 | 2.0971
99 | 1.0032 | -146.8792 | 0.996 | 95.7965 | 1.0105 | -24.5279 | 1.8902

## node_sequence_components
node | U0_abs_pu | U1_abs_pu | U2_abs_pu | alpha0 | alpha2
0 | 5.1403e-14 | 1.05 | 1.9837e-06 | 4.8956e-14 | 1.8892e-06
1 | 0.00041927 | 1.0387 | 0.0035806 | 0.00040365 | 0.0034471
10 | 0.00089931 | 1.0389 | 0.0078202 | 0.00086564 | 0.0075274
100 | 0.011576 | 0.99913 | 0.017972 | 0.011586 | 0.017988
101 | 0.012612 | 0.99522 | 0.017027 | 0.012673 | 0.017109
102 | 0.0090624 | 1.011 | 0.020012 | 0.0089634 | 0.019794
103 | 0.0057112 | 1.0269 | 0.021485 | 0.0055618 | 0.020923
104 | 0.0097812 | 1.008 | 0.019788 | 0.0097038 | 0.019631
105 | 0.0057212 | 1.0264 | 0.021551 | 0.0055739 | 0.020996
106 | 0.0057138 | 1.0263 | 0.021729 | 0.0055675 | 0.021173
107 | 0.0057047 | 1.0269 | 0.021512 | 0.0055552 | 0.020948
108 | 0.01259 | 0.99506 | 0.017034 | 0.012653 | 0.017119
109 | 0.010458 | 1.003 | 0.019083 | 0.010427 | 0.019027
11 | 0.0013298 | 1.0387 | 0.011555 | 0.0012803 | 0.011125
110 | 0.012574 | 0.99488 | 0.017018 | 0.012639 | 0.017105
111 | 0.0084446 | 1.0152 | 0.020622 | 0.0083185 | 0.020314
112 | 0.0085009 | 1.0156 | 0.020674 | 0.0083701 | 0.020356
113 | 0.01014 | 1.0031 | 0.019571 | 0.010109 | 0.01951
114 | 0.012574 | 0.99464 | 0.017034 | 0.012642 | 0.017126
115 | 0.0085011 | 1.0159 | 0.020851 | 0.0083683 | 0.020525
116 | 0.010445 | 1.0025 | 0.019083 | 0.010418 | 0.019034
12 | 0.0013298 | 1.0385 | 0.01138 | 0.0012805 | 0.010958
13 | 0.0011763 | 1.0401 | 0.0098612 | 0.0011309 | 0.0094806
14 | 0.0016221 | 1.0393 | 0.013403 | 0.0015607 | 0.012896
15 | 0.0019233 | 1.0393 | 0.014914 | 0.0018505 | 0.01435
16 | 0.0019183 | 1.0393 | 0.014956 | 0.0018458 | 0.014391
17 | 0.0019125 | 1.0391 | 0.014998 | 0.0018405 | 0.014434
18 | 0.0019115 | 1.0392 | 0.015056 | 0.0018394 | 0.014489
19 | 0.00162 | 1.0394 | 0.013675 | 0.0015586 | 0.013156
2 | 0.00090021 | 1.0392 | 0.0077311 | 0.00086624 | 0.0074393
20 | 0.001616 | 1.0395 | 0.013832 | 0.0015545 | 0.013306
21 | 0.0015826 | 1.0393 | 0.013989 | 0.0015227 | 0.01346
22 | 0.0016151 | 1.0397 | 0.013872 | 0.0015534 | 0.013343
23 | 0.0016132 | 1.0395 | 0.013948 | 0.0015519 | 0.013418
24 | 0.0016094 | 1.0394 | 0.014064 | 0.0015484 | 0.013531
25 | 0.001613 | 1.0395 | 0.014048 | 0.0015517 | 0.013515
26 | 0.0016218 | 1.04 | 0.013949 | 0.0015594 | 0.013413
27 | 0.0016057 | 1.0393 | 0.01418 | 0.001545 | 0.013644
28 | 0.0022388 | 1.0394 | 0.016334 | 0.0021538 | 0.015715
29 | 0.0016036 | 1.0391 | 0.014356 | 0.0015432 | 0.013816
3 | 0.00090048 | 1.0393 | 0.0078202 | 0.00086643 | 0.0075245
30 | 0.0016036 | 1.0391 | 0.014356 | 0.0015432 | 0.013816
31 | 0.0019081 | 1.0389 | 0.014983 | 0.0018366 | 0.014421
32 | 0.0025521 | 1.0391 | 0.01779 | 0.002456 | 0.01712
33 | 0.0016234 | 1.0404 | 0.013782 | 0.0015604 | 0.013248
34 | 0.0019056 | 1.0388 | 0.014896 | 0.0018345 | 0.01434
35 | 0.0028615 | 1.0386 | 0.019252 | 0.0027552 | 0.018537
36 | 0.0019105 | 1.0392 | 0.015114 | 0.0018384 | 0.014544
37 | 0.0019276 | 1.0397 | 0.014958 | 0.0018539 | 0.014386
38 | 0.0027835 | 1.039 | 0.02032 | 0.002679 | 0.019557
39 | 0.0019056 | 1.0385 | 0.014983 | 0.0018349 | 0.014427
4 | 0.0011678 | 1.0395 | 0.0098765 | 0.0011234 | 0.0095015
40 | 0.0019202 | 1.0399 | 0.015292 | 0.0018465 | 0.014705
41 | 0.0027238 | 1.0397 | 0.02095 | 0.0026198 | 0.02015
42 | 0.001908 | 1.0388 | 0.015114 | 0.0018367 | 0.01455
43 | 0.0026832 | 1.0406 | 0.021435 | 0.0025787 | 0.0206
44 | 0.0027809 | 1.0389 | 0.020492 | 0.0026768 | 0.019725
45 | 0.0027207 | 1.0396 | 0.021007 | 0.0026169 | 0.020206
46 | 0.0025547 | 1.0393 | 0.017786 | 0.0024581 | 0.017114
47 | 0.0027773 | 1.0387 | 0.020669 | 0.0026738 | 0.019899
48 | 0.0032435 | 1.0377 | 0.019739 | 0.0031257 | 0.019022
49 | 0.0022403 | 1.0397 | 0.016311 | 0.0021547 | 0.015688
5 | 0.00091242 | 1.0407 | 0.0081638 | 0.00087676 | 0.0078447
50 | 0.002725 | 1.0388 | 0.020816 | 0.0026231 | 0.020038
51 | 0.0036178 | 1.0365 | 0.020252 | 0.0034903 | 0.019538
52 | 0.0026802 | 1.0405 | 0.021492 | 0.0025759 | 0.020656
53 | 0.00266 | 1.0416 | 0.021777 | 0.0025538 | 0.020908
54 | 0.0032463 | 1.0378 | 0.019731 | 0.0031281 | 0.019012
55 | 0.0026396 | 1.0421 | 0.021993 | 0.002533 | 0.021104
56 | 0.0026335 | 1.0419 | 0.02198 | 0.0025276 | 0.021096
57 | 0.0026301 | 1.0415 | 0.02198 | 0.0025253 | 0.021105
58 | 0.0039935 | 1.0351 | 0.020536 | 0.0038582 | 0.01984
59 | 0.0026422 | 1.0431 | 0.022241 | 0.002533 | 0.021322
6 | 0.0011694 | 1.0397 | 0.0098602 | 0.0011248 | 0.0094837
60 | 0.0039937 | 1.0355 | 0.020502 | 0.0038567 | 0.019799
61 | 0.0036173 | 1.0368 | 0.020428 | 0.003489 | 0.019703
62 | 0.0036213 | 1.0375 | 0.020581 | 0.0034904 | 0.019838
63 | 0.0026468 | 1.0434 | 0.022296 | 0.0025367 | 0.021368
64 | 0.0036126 | 1.0366 | 0.020605 | 0.003485 | 0.019877
65 | 0.0026374 | 1.0434 | 0.022351 | 0.0025277 | 0.021422
66 | 0.0026598 | 1.0441 | 0.022472 | 0.0025474 | 0.021522
67 | 0.0026301 | 1.0417 | 0.021902 | 0.0025247 | 0.021025
68 | 0.0043949 | 1.0331 | 0.020899 | 0.0042539 | 0.020228
69 | 0.0026219 | 1.0429 | 0.022321 | 0.0025141 | 0.021403
7 | 0.0011834 | 1.0412 | 0.0096445 | 0.0011366 | 0.0092632
70 | 0.0026143 | 1.0427 | 0.022291 | 0.0025072 | 0.021377
71 | 0.0047904 | 1.0307 | 0.021345 | 0.0046476 | 0.020709
72 | 0.0026593 | 1.0439 | 0.022295 | 0.0025475 | 0.021358
73 | 0.004778 | 1.0307 | 0.021433 | 0.0046357 | 0.020795
74 | 0.0052452 | 1.0284 | 0.021499 | 0.0051003 | 0.020905
75 | 0.0026189 | 1.0427 | 0.022321 | 0.0025116 | 0.021406
76 | 0.0026624 | 1.0418 | 0.021827 | 0.0025556 | 0.020952
77 | 0.0026113 | 1.0427 | 0.022279 | 0.0025045 | 0.021368
78 | 0.0026422 | 1.0437 | 0.022407 | 0.0025316 | 0.021469
79 | 0.0057361 | 1.0263 | 0.021514 | 0.0055894 | 0.020964
8 | 0.001337 | 1.0392 | 0.011277 | 0.0012865 | 0.010852
80 | 0.0026557 | 1.0441 | 0.022407 | 0.0025434 | 0.02146
81 | 0.0026562 | 1.0444 | 0.022583 | 0.0025434 | 0.021624
82 | 0.0062708 | 1.0236 | 0.021502 | 0.006126 | 0.021005
83 | 0.0052407 | 1.0284 | 0.021541 | 0.0050962 | 0.020947
84 | 0.0062402 | 1.0238 | 0.021569 | 0.0060954 | 0.021069
85 | 0.0069412 | 1.0206 | 0.021271 | 0.006801 | 0.020841
86 | 0.0076666 | 1.0178 | 0.020913 | 0.0075328 | 0.020548
87 | 0.0062224 | 1.0242 | 0.021531 | 0.0060752 | 0.021021
88 | 0.0069353 | 1.0206 | 0.021313 | 0.0067955 | 0.020883
89 | 0.0084153 | 1.0149 | 0.020567 | 0.0082918 | 0.020265
9 | 0.0013315 | 1.0389 | 0.01138 | 0.0012817 | 0.010954
90 | 0.0090827 | 1.0112 | 0.020057 | 0.0089825 | 0.019835
91 | 0.0090742 | 1.0112 | 0.020059 | 0.0089736 | 0.019836
92 | 0.009789 | 1.0072 | 0.019564 | 0.0097191 | 0.019425
93 | 0.0090881 | 1.0117 | 0.020074 | 0.0089831 | 0.019842
94 | 0.0097764 | 1.0073 | 0.019605 | 0.0097059 | 0.019464
95 | 0.0060666 | 1.0239 | 0.021846 | 0.005925 | 0.021335
96 | 0.0097636 | 1.0068 | 0.019605 | 0.0096972 | 0.019472
97 | 0.0043974 | 1.0333 | 0.020876 | 0.0042557 | 0.020203
98 | 0.0057279 | 1.0264 | 0.021525 | 0.0055806 | 0.020971
99 | 0.010542 | 1.003 | 0.018959 | 0.01051 | 0.018902

## transformer_phase_results
transformer | I_tr_L1_A | angle_I_tr_L1_deg | P_tr_L1_kW | Q_tr_L1_kvar | I_tr_L2_A | angle_I_tr_L2_deg | P_tr_L2_kW | Q_tr_L2_kvar | I_tr_L3_A | angle_I_tr_L3_deg | P_tr_L3_kW | Q_tr_L3_kvar | loading_percent | I_neutral_A
TR1 | 70.7638 | -79.2513 | 5.7027 | -16.0462 | 111.4729 | 172.8353 | 3.4844 | -26.4391 | 119.0563 | 32.7116 | 13.3637 | -25.2237 | 36.5318 | 9.1494

## pv_setpoints
name | P_kW | Q_kvar | Q_set_kvar | S_apparent_kVA | Smax_kVA | av_mode
PV102F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV102F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV102F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV103F1 | 1.76 | -0.58157 | 0 | 1.8536 | 10 | qvchar
PV103F2 | 1.76 | -1.6906e-09 | 0 | 1.76 | 10 | qvchar
PV103F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV104F1 | 1.76 | 1.3743e-08 | 0 | 1.76 | 10 | qvchar
PV104F2 | 1.76 | -2.2971e-09 | 0 | 1.76 | 10 | qvchar
PV104F3 | 1.76 | 4.528e-10 | 0 | 1.76 | 10 | qvchar
PV106F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV106F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV106F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV107F1 | 1.76 | -0.58159 | 0 | 1.8536 | 10 | qvchar
PV107F2 | 1.76 | -1.696e-09 | 0 | 1.76 | 10 | qvchar
PV107F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV10F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV10F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV10F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV110F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV110F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV110F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV112F1 | 1.76 | 1.3721e-08 | 0 | 1.76 | 10 | qvchar
PV112F2 | 1.76 | -2.1347e-09 | 0 | 1.76 | 10 | qvchar
PV112F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV113F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV113F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV113F3 | 2 | 5.3596e-10 | 0 | 2 | 10 | qvchar
PV114F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV114F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV114F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV115F1 | 1.76 | 2.4994e-08 | 0 | 1.76 | 10 | qvchar
PV115F2 | 1.76 | -2.1356e-09 | 0 | 1.76 | 10 | qvchar
PV115F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV116F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV116F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV116F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV11F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV11F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV11F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV12F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV12F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV12F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV13F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV13F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV13F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV21F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV21F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV21F3 | 2 | -0.66 | 0 | 2.1061 | 10 | qvchar
PV25F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV25F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV25F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV26F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV26F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV26F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV29F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV29F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV29F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV30F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV30F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV30F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV33F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV33F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV33F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV34F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV34F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV34F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV37F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV37F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV37F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV39F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV39F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV39F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV40F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV40F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV40F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV42F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV42F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV42F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV45F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV45F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV45F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV46F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV46F2 | 1.76 | -0.48553 | 0 | 1.8257 | 10 | qvchar
PV46F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV47F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV47F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV47F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV49F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV49F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV49F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV50F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV50F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV50F3 | 2 | -0.65998 | 0 | 2.1061 | 10 | qvchar
PV52F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV52F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV52F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV54F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV54F2 | 1.76 | -0.22942 | 0 | 1.7749 | 10 | qvchar
PV54F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV57F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV57F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV57F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV5F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV5F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV5F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV60F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV60F2 | 1.76 | -0.01827 | 0 | 1.7601 | 10 | qvchar
PV60F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV62F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV62F2 | 1.76 | -0.15588 | 0 | 1.7669 | 10 | qvchar
PV62F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV64F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV64F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV64F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV66F1 | 1.76 | -0.58081 | 0 | 1.8534 | 10 | qvchar
PV66F2 | 1.76 | -0.53981 | 0 | 1.8409 | 10 | qvchar
PV66F3 | 1.76 | -0.58076 | 0 | 1.8533 | 10 | qvchar
PV67F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV67F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV67F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV72F1 | 1.76 | -0.58081 | 0 | 1.8534 | 10 | qvchar
PV72F2 | 1.76 | -0.5339 | 0 | 1.8392 | 10 | qvchar
PV72F3 | 1.76 | -0.58076 | 0 | 1.8533 | 10 | qvchar
PV73F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV73F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV73F3 | 2 | -0.66 | 0 | 2.1061 | 10 | qvchar
PV75F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV75F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV75F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV76F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV76F2 | 1.76 | -0.36813 | 0 | 1.7981 | 10 | qvchar
PV76F3 | 1.76 | -0.58077 | 0 | 1.8533 | 10 | qvchar
PV77F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV77F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV77F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV7F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV7F2 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV7F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV80F1 | 1.76 | -0.58081 | 0 | 1.8534 | 10 | qvchar
PV80F2 | 1.76 | -0.54965 | 0 | 1.8438 | 10 | qvchar
PV80F3 | 1.76 | -0.58076 | 0 | 1.8533 | 10 | qvchar
PV81F1 | 1.76 | -0.58081 | 0 | 1.8534 | 10 | qvchar
PV81F2 | 1.76 | -0.55556 | 0 | 1.8456 | 10 | qvchar
PV81F3 | 1.76 | -0.58075 | 0 | 1.8533 | 10 | qvchar
PV83F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV83F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV83F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV87F1 | 1.76 | -0.564 | 0 | 1.8482 | 10 | qvchar
PV87F2 | 1.76 | -1.8209e-09 | 0 | 1.76 | 10 | qvchar
PV87F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV88F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV88F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV88F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV93F1 | 1.76 | 1.3737e-08 | 0 | 1.76 | 10 | qvchar
PV93F2 | 1.76 | -2.223e-09 | 0 | 1.76 | 10 | qvchar
PV93F3 | 1.76 | -0.10305 | 0 | 1.763 | 10 | qvchar
PV95F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV95F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV95F3 | 2 | -0.66 | 0 | 2.1061 | 10 | qvchar
PV96F1 | 0 | 0 | 0 | 0 | 10 | qvchar
PV96F2 | 0 | 0 | 0 | 0 | 10 | qvchar
PV96F3 | 0 | 0 | 0 | 0 | 10 | qvchar
PV97F1 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar
PV97F2 | 1.76 | -1.1978e-09 | 0 | 1.76 | 10 | qvchar
PV97F3 | 1.76 | -0.5808 | 0 | 1.8534 | 10 | qvchar

## storage_setpoints
node | element | phase | step_label | step_pu | search_direction | u_before_pu | u_after_pu | voltage_error_abs | p_storage_kw | q_storage_kvar | Pmax_kW | Smax_kVA | p_storage_kw_in_model | q_storage_kvar_in_model
101 | ES101F1 | L1 | 3 | 0.3 | start | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | -9 | 0
101 | ES101F2 | L2 | 1 | 0.1 | start | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | -3 | 0
101 | ES101F3 | L3 | 4 | 0.4 | start | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | -12 | 0

## branch_losses
branch | P_loss_kW | Q_loss_kvar | loading_percent
Ln1.2 | 1.3718 | 0.43096 | 55.895
Ln100.101 | 0.12425 | 0.039033 | 33.9957
Ln101.108 | 0.00065039 | 0.00020433 | 4.6358
Ln105.106 | 0.00038929 | 1.9247e-05 | 4.1966
Ln105.107 | 0.0020342 | 0.00010057 | 7.0874
Ln108.110 | 0.00045376 | 2.2434e-05 | 3.0118
Ln108.114 | 0.0011739 | 5.8041e-05 | 5.6889
Ln109.113 | 0.0021951 | 0.00010853 | 10.2139
Ln109.116 | 0.0011357 | 5.6153e-05 | 5.4624
Ln111.112 | 0.0017577 | 8.6902e-05 | 6.1814
Ln111.115 | 0.0035549 | 0.00017576 | 9.7193
Ln14.15 | 0.3599 | 0.11306 | 51.22
Ln14.19 | 0.0046108 | 0.0014485 | 13.532
Ln15.16 | 0.0023459 | 0.00073698 | 8.2256
Ln15.28 | 0.27832 | 0.087437 | 46.1314
Ln16.17 | 0.0010031 | 0.00031512 | 5.7649
Ln16.37 | 0.0023362 | 0.0001155 | 6.9378
Ln17.18 | 0.00065908 | 0.00020706 | 4.2779
Ln17.31 | 0.00071464 | 0.00022451 | 4.4591
Ln18.36 | 0.00065908 | 0.00020706 | 4.2779
Ln19.20 | 0.0028975 | 0.00091028 | 9.0965
Ln19.21 | 0.0017012 | 8.4111e-05 | 7.7914
Ln2.3 | 0.00098503 | 0.00030946 | 4.3881
Ln2.4 | 0.58926 | 0.18512 | 67.2935
Ln20.22 | 0.00090372 | 0.00028391 | 4.7831
Ln20.23 | 0.0007979 | 0.00025067 | 5.029
Ln22.25 | 0.00036237 | 1.7916e-05 | 3.8232
Ln22.33 | 0.0037763 | 0.00018671 | 10.321
Ln23.24 | 0.00046848 | 0.00014718 | 4.3817
Ln23.26 | 0.0023345 | 0.00011542 | 6.9268
Ln24.27 | 0.00046848 | 0.00014718 | 4.3817
Ln27.29 | 0.00036286 | 1.794e-05 | 3.827
Ln27.30 | 0.00036286 | 1.794e-05 | 3.827
Ln28.32 | 0.24398 | 0.07665 | 43.8789
Ln28.49 | 0.0019544 | 0.00061399 | 5.9274
Ln3.10 | 0.0010149 | 5.0176e-05 | 4.5026
Ln3.5 | 0.0075044 | 0.00037103 | 10.0462
Ln31.34 | 0.0003515 | 1.7378e-05 | 3.5182
Ln31.39 | 0.0010168 | 5.0271e-05 | 4.5483
Ln32.35 | 0.21373 | 0.067145 | 41.1306
Ln32.46 | 0.0010951 | 0.00034404 | 3.879
Ln35.38 | 0.0479 | 0.015048 | 20.0267
Ln35.48 | 0.072561 | 0.022796 | 23.0009
Ln36.40 | 0.0037525 | 0.00018553 | 9.9113
Ln36.42 | 0.0010162 | 5.0242e-05 | 4.5483
Ln38.41 | 0.03966 | 0.01246 | 16.0618
Ln38.44 | 0.00093451 | 0.00029358 | 4.8328
Ln4.6 | 0.0028265 | 0.00088798 | 9.7275
Ln4.8 | 0.30605 | 0.096149 | 61.9623
Ln41.43 | 0.040082 | 0.012592 | 15.6535
Ln41.45 | 0.00011903 | 3.7395e-05 | 2.2411
Ln43.52 | 0.00011891 | 3.7355e-05 | 2.2455
Ln43.53 | 0.041119 | 0.012918 | 15.7644
Ln44.47 | 0.00036936 | 1.8262e-05 | 3.9005
Ln44.50 | 0.0016594 | 8.2043e-05 | 7.6565
Ln48.51 | 0.061525 | 0.019329 | 20.9709
Ln48.54 | 0.00050823 | 0.00015967 | 3.9009
Ln51.58 | 0.053864 | 0.016922 | 19.2765
Ln51.61 | 0.0016791 | 0.00052751 | 5.8086
Ln53.55 | 0.024408 | 0.0076679 | 13.0649
Ln53.76 | 0.001156 | 0.00036318 | 5.6083
Ln55.56 | 0.00071207 | 0.0002237 | 4.3777
Ln55.59 | 0.02909 | 0.0091389 | 12.8954
Ln56.57 | 0.0010124 | 5.0055e-05 | 4.6043
Ln56.67 | 0.00035058 | 1.7333e-05 | 3.4486
Ln58.60 | 0.0020124 | 9.9496e-05 | 6.8721
Ln58.68 | 0.054932 | 0.017257 | 18.8834
Ln59.63 | 0.0036853 | 0.0011578 | 9.2127
Ln59.65 | 0.0061252 | 0.0019243 | 6.5554
Ln6.13 | 0.0023323 | 0.00011531 | 6.8536
Ln6.7 | 0.0080318 | 0.00039711 | 10.2401
Ln61.62 | 0.0035008 | 0.00017308 | 9.7559
Ln61.64 | 0.00037305 | 1.8444e-05 | 3.9721
Ln63.66 | 0.0036848 | 0.00018218 | 9.7823
Ln63.72 | 0.0022805 | 0.00011275 | 6.791
Ln65.69 | 0.0017993 | 0.00056527 | 3.5991
Ln65.78 | 0.0036996 | 0.0011623 | 9.2129
Ln68.71 | 0.060156 | 0.018898 | 19.4699
Ln68.97 | 0.00083219 | 0.00026144 | 5.3244
Ln69.70 | 0.00028611 | 8.9883e-05 | 1.6243
Ln69.75 | 0.00032599 | 0.00010241 | 2.6391
Ln70.77 | 0.00011299 | 3.5496e-05 | 1.9774
Ln71.73 | 0.00039721 | 0.00012479 | 4.3183
Ln71.74 | 0.052485 | 0.016489 | 17.7989
Ln74.79 | 0.048038 | 0.015091 | 16.7787
Ln74.83 | 9.3315e-05 | 2.9316e-05 | 2.3686
Ln78.80 | 0.0022923 | 0.00011333 | 6.8396
Ln78.81 | 0.0036951 | 0.00018269 | 9.7826
Ln79.82 | 0.052287 | 0.016427 | 17.3381
Ln79.98 | 0.0016631 | 0.00052246 | 7.4787
Ln8.14 | 0.48408 | 0.15208 | 61.7016
Ln8.9 | 0.0012619 | 0.00039643 | 4.7712
Ln82.84 | 0.0012147 | 0.00038162 | 8.454
Ln82.85 | 0.065698 | 0.02064 | 22.4161
Ln84.87 | 0.0020299 | 0.00010036 | 7.0996
Ln84.95 | 0.0016624 | 8.2192e-05 | 8.992
Ln85.86 | 0.060635 | 0.019049 | 21.9737
Ln85.88 | 9.6711e-05 | 3.0383e-05 | 2.4885
Ln86.89 | 0.060635 | 0.019049 | 21.9737
Ln89.111 | 0.0024409 | 0.00076682 | 9.05
Ln89.90 | 0.10171 | 0.031952 | 27.9118
Ln9.11 | 0.00036098 | 1.7847e-05 | 3.8166
Ln9.12 | 0.0010161 | 5.0238e-05 | 4.5179
Ln90.91 | 0.00026894 | 8.449e-05 | 3.4551
Ln90.92 | 0.11251 | 0.035345 | 29.4012
Ln91.102 | 0.00040711 | 2.0128e-05 | 3.135
Ln91.93 | 0.0015455 | 7.6411e-05 | 6.1412
Ln92.94 | 0.00028051 | 8.8124e-05 | 3.151
Ln92.99 | 0.12794 | 0.040195 | 31.3848
Ln94.104 | 0.0033289 | 0.00016458 | 9.0942
Ln94.96 | 0.0011206 | 5.5405e-05 | 5.3848
Ln98.103 | 0.0020344 | 0.00010058 | 7.0885
Ln98.105 | 0.00038619 | 0.00012132 | 3.9396
Ln99.100 | 0.12425 | 0.039033 | 33.9958
Ln99.109 | 0.00063522 | 0.00019956 | 5.8302

## iteration_history
stage | iteration | critical_node | storage_L1 | storage_L2 | storage_L3 | U_L1_pu_final | U_L2_pu_final | U_L3_pu_final | selected_step_label_L1 | selected_step_pu_L1 | P_storage_L1_kW | U_before_L1_pu | U_after_L1_pu | voltage_error_L1 | selected_step_label_L2 | selected_step_pu_L2 | P_storage_L2_kW | U_before_L2_pu | U_after_L2_pu | voltage_error_L2 | selected_step_label_L3 | selected_step_pu_L3 | P_storage_L3_kW | U_before_L3_pu | U_after_L3_pu | voltage_error_L3
control | 1 | 101 | ES101F1 | ES101F2 | ES101F3 | 0.99453 | 0.99224 | 0.99954 | 3 | 0.3 | 9 | 1.0676 | 1.0071 | 0.0071139 | 1 | 0.1 | 3 | 1.0178 | 1.0028 | 0.0027839 | 4 | 0.4 | 12 | 1.0775 | 0.99954 | 0.00046288
control | 2 | 101 | ES101F1 | ES101F2 | ES101F3 | 0.99453 | 0.99224 | 0.99954 | 3 | 0.3 | 9 | 0.99453 | 0.99453 | 0.0054693 | 1 | 0.1 | 3 | 0.99224 | 0.99224 | 0.0077557 | 4 | 0.4 | 12 | 0.99954 | 0.99954 | 0.00046288
control | 3 | 101 | ES101F1 | ES101F2 | ES101F3 | 0.99453 | 0.99224 | 0.99954 | 3 | 0.3 | 9 | 0.99453 | 0.99453 | 0.0054693 | 1 | 0.1 | 3 | 0.99224 | 0.99224 | 0.0077557 | 4 | 0.4 | 12 | 0.99954 | 0.99954 | 0.00046288

## phase_search_history
iteration | phase | search_stage | u_before_pu | tested_step_label | tested_step_pu | u_after_pu | voltage_error_abs | converged | loadflow_result | direction
1 | L1 | direction_test_positive | 1.0676 | 1 | 0.1 | 1.0468 | 0.046844 | TRUE | 0
1 | L1 | direction_test_negative | 1.0676 | -1 | -0.1 | 1.0883 | 0.088323 | TRUE | 0
1 | L1 | monotonic_search | 1.0676 | 1 | 0.1 | 1.0468 | 0.046844 | TRUE | 0 | positive
1 | L1 | monotonic_search | 1.0676 | 2 | 0.2 | 1.026 | 0.026039 | TRUE | 0 | positive
1 | L1 | monotonic_search | 1.0676 | 3 | 0.3 | 1.0071 | 0.0071139 | TRUE | 0 | positive
1 | L1 | monotonic_search | 1.0676 | 4 | 0.4 | 0.99129 | 0.0087054 | TRUE | 0 | positive
1 | L2 | direction_test_positive | 1.0178 | 1 | 0.1 | 1.0028 | 0.0027839 | TRUE | 0
1 | L2 | direction_test_negative | 1.0178 | -1 | -0.1 | 1.0325 | 0.032457 | TRUE | 0
1 | L2 | monotonic_search | 1.0178 | 1 | 0.1 | 1.0028 | 0.0027839 | TRUE | 0 | positive
1 | L2 | monotonic_search | 1.0178 | 2 | 0.2 | 0.98288 | 0.017124 | TRUE | 0 | positive
1 | L3 | direction_test_positive | 1.0775 | 1 | 0.1 | 1.0576 | 0.057637 | TRUE | 0
1 | L3 | direction_test_negative | 1.0775 | -1 | -0.1 | 1.0969 | 0.096921 | TRUE | 0
1 | L3 | monotonic_search | 1.0775 | 1 | 0.1 | 1.0576 | 0.057637 | TRUE | 0 | positive
1 | L3 | monotonic_search | 1.0775 | 2 | 0.2 | 1.0368 | 0.036812 | TRUE | 0 | positive
1 | L3 | monotonic_search | 1.0775 | 3 | 0.3 | 1.0159 | 0.015916 | TRUE | 0 | positive
1 | L3 | monotonic_search | 1.0775 | 4 | 0.4 | 0.99954 | 0.00046288 | TRUE | 0 | positive
1 | L3 | monotonic_search | 1.0775 | 5 | 0.5 | 0.9804 | 0.019596 | TRUE | 0 | positive
2 | L1 | direction_test_positive | 0.99453 | 1 | 0.1 | 1.0313 | 0.031314 | TRUE | 0
2 | L1 | direction_test_negative | 0.99453 | -1 | -0.1 | 1.0732 | 0.073189 | TRUE | 0
2 | L1 | monotonic_search | 0.99453 | -1 | -0.1 | 1.0732 | 0.073189 | TRUE | 0 | negative
2 | L2 | direction_test_positive | 0.99224 | 1 | 0.1 | 0.99224 | 0.0077557 | TRUE | 0
2 | L2 | direction_test_negative | 0.99224 | -1 | -0.1 | 1.0227 | 0.022653 | TRUE | 0
2 | L2 | monotonic_search | 0.99224 | -1 | -0.1 | 1.0227 | 0.022653 | TRUE | 0 | negative
2 | L3 | direction_test_positive | 0.99954 | 1 | 0.1 | 1.0576 | 0.057637 | TRUE | 0
2 | L3 | direction_test_negative | 0.99954 | -1 | -0.1 | 1.0969 | 0.096921 | TRUE | 0
2 | L3 | monotonic_search | 0.99954 | -1 | -0.1 | 1.0969 | 0.096921 | TRUE | 0 | negative
3 | L1 | direction_test_positive | 0.99453 | 1 | 0.1 | 1.0313 | 0.031314 | TRUE | 0
3 | L1 | direction_test_negative | 0.99453 | -1 | -0.1 | 1.0732 | 0.073189 | TRUE | 0
3 | L1 | monotonic_search | 0.99453 | -1 | -0.1 | 1.0732 | 0.073189 | TRUE | 0 | negative
3 | L2 | direction_test_positive | 0.99224 | 1 | 0.1 | 0.99224 | 0.0077557 | TRUE | 0
3 | L2 | direction_test_negative | 0.99224 | -1 | -0.1 | 1.0227 | 0.022653 | TRUE | 0
3 | L2 | monotonic_search | 0.99224 | -1 | -0.1 | 1.0227 | 0.022653 | TRUE | 0 | negative
3 | L3 | direction_test_positive | 0.99954 | 1 | 0.1 | 1.0576 | 0.057637 | TRUE | 0
3 | L3 | direction_test_negative | 0.99954 | -1 | -0.1 | 1.0969 | 0.096921 | TRUE | 0
3 | L3 | monotonic_search | 0.99954 | -1 | -0.1 | 1.0969 | 0.096921 | TRUE | 0 | negative

## loadflow_attempts
stage | attempt_no | critical_node | storage_element | phase | search_direction | step_label | step_pu | u_before_pu | u_after_pu | voltage_error_abs | p_storage_kw | q_storage_kvar | Pmax_kW | Smax_kVA | converged | loadflow_result | note
initial | 0 | 101 | ES101F1 | L1 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | first loadflow after switching PV to qvchar and storage=0
initial | 0 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | first loadflow after switching PV to qvchar and storage=0
initial | 0 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | first loadflow after switching PV to qvchar and storage=0
phase_search | 1 | 101 | ES101F1 | L1 | direction_test_positive | 1 | 0.1 | 1.0676 | 1.0468 | 0.046844 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 1 | 101 | ES101F1 | L1 | direction_test_negative | -1 | -0.1 | 1.0676 | 1.0883 | 0.088323 | -3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 1 | 101 | ES101F1 | L1 | positive | 1 | 0.1 | 1.0676 | 1.0468 | 0.046844 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 2 | 0.2 | 1.0676 | 1.026 | 0.026039 | 6 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 4 | 0.4 | 1.0676 | 0.99129 | 0.0087054 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_restore | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 1 | 101 | ES101F2 | L2 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 1 | 101 | ES101F2 | L2 | direction_test_positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 1 | 101 | ES101F2 | L2 | direction_test_negative | -1 | -0.1 | 1.0178 | 1.0325 | 0.032457 | -3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 2 | 0.2 | 1.0178 | 0.98288 | 0.017124 | 6 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_restore | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 1 | 101 | ES101F3 | L3 | start | 0 | 0 |  |  |  | 0 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 1 | 101 | ES101F3 | L3 | direction_test_positive | 1 | 0.1 | 1.0775 | 1.0576 | 0.057637 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 1 | 101 | ES101F3 | L3 | direction_test_negative | -1 | -0.1 | 1.0775 | 1.0969 | 0.096921 | -3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | positive | 1 | 0.1 | 1.0775 | 1.0576 | 0.057637 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | positive | 2 | 0.2 | 1.0775 | 1.0368 | 0.036812 | 6 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | positive | 3 | 0.3 | 1.0775 | 1.0159 | 0.015916 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 1 | 101 | ES101F3 | L3 | positive | 5 | 0.5 | 1.0775 | 0.9804 | 0.019596 | 15 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_restore | 1 | 101 | ES101F1 | L1 | positive | 3 | 0.3 | 1.0676 | 1.0071 | 0.0071139 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 1 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 1 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_search | 2 | 101 | ES101F1 | L1 | direction_test_positive | 1 | 0.1 | 0.99453 | 1.0313 | 0.031314 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 2 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 2 | 101 | ES101F1 | L1 | direction_test_negative | -1 | -0.1 | 0.99453 | 1.0732 | 0.073189 | -3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 2 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 2 | 101 | ES101F1 | L1 | negative | -1 | -0.1 | 0.99453 | 1.0732 | 0.073189 | -3 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 2 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_restore | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 2 | 101 | ES101F2 | L2 | positive | 1 | 0.1 | 1.0178 | 1.0028 | 0.0027839 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 2 | 101 | ES101F2 | L2 | direction_test_positive | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 2 | 101 | ES101F2 | L2 | direction_test_negative | -1 | -0.1 | 0.99224 | 1.0227 | 0.022653 | -3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 2 | 101 | ES101F2 | L2 | negative | -1 | -0.1 | 0.99224 | 1.0227 | 0.022653 | -3 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_restore | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 2 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 2 | 101 | ES101F3 | L3 | positive | 4 | 0.4 | 1.0775 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 2 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 2 | 101 | ES101F3 | L3 | direction_test_positive | 1 | 0.1 | 0.99954 | 1.0576 | 0.057637 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 2 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 2 | 101 | ES101F3 | L3 | direction_test_negative | -1 | -0.1 | 0.99954 | 1.0969 | 0.096921 | -3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 2 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 2 | 101 | ES101F3 | L3 | negative | -1 | -0.1 | 0.99954 | 1.0969 | 0.096921 | -3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_restore | 2 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 2 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 2 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_search | 3 | 101 | ES101F1 | L1 | direction_test_positive | 1 | 0.1 | 0.99453 | 1.0313 | 0.031314 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest positive step
phase_search | 3 | 101 | ES101F1 | L1 | direction_test_negative | -1 | -0.1 | 0.99453 | 1.0732 | 0.073189 | -3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: test smallest negative step
phase_search | 3 | 101 | ES101F1 | L1 | negative | -1 | -0.1 | 0.99453 | 1.0732 | 0.073189 | -3 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: search step from Excel
phase_restore | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_restore | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L1: restore best after deterioration
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 3 | 101 | ES101F2 | L2 | direction_test_positive | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest positive step
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 3 | 101 | ES101F2 | L2 | direction_test_negative | -1 | -0.1 | 0.99224 | 1.0227 | 0.022653 | -3 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: test smallest negative step
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 3 | 101 | ES101F2 | L2 | negative | -1 | -0.1 | 0.99224 | 1.0227 | 0.022653 | -3 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_search | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: search step from Excel
phase_restore | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_restore | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L2: restore best after deterioration
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 3 | 101 | ES101F3 | L3 | direction_test_positive | 1 | 0.1 | 0.99954 | 1.0576 | 0.057637 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest positive step
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 3 | 101 | ES101F3 | L3 | direction_test_negative | -1 | -0.1 | 0.99954 | 1.0969 | 0.096921 | -3 | 0 | 30 | 35 | TRUE | 0 | L3: test smallest negative step
phase_search | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_search | 3 | 101 | ES101F3 | L3 | negative | -1 | -0.1 | 0.99954 | 1.0969 | 0.096921 | -3 | 0 | 30 | 35 | TRUE | 0 | L3: search step from Excel
phase_restore | 3 | 101 | ES101F1 | L1 | start | 3 | 0.3 | 0.99453 | 0.99453 | 0.0054693 | 9 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 3 | 101 | ES101F2 | L2 | start | 1 | 0.1 | 0.99224 | 0.99224 | 0.0077557 | 3 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration
phase_restore | 3 | 101 | ES101F3 | L3 | start | 4 | 0.4 | 0.99954 | 0.99954 | 0.00046288 | 12 | 0 | 30 | 35 | TRUE | 0 | L3: restore best after deterioration

## indicators
Umax_pu | Umin_pu | Udev_mean_pu | Udev_max_pu | Fcelu_1_Udev_rms_1_00 | Fcelu_1_Udev_rms_1_05 | dU_phase_max_pu | kU2_max_percent | alpha0_mean | alpha0_max | alpha2_mean | alpha2_max | Fcelu_3_weighted | I_tr_L1_A | I_tr_L2_A | I_tr_L3_A | I_unbalance_tr_percent | I_neutral_A | P_tr_L1_kW | P_tr_L2_kW | P_tr_L3_kW | P_export_total_kW | P_import_total_kW | P_loss_total_kW | Q_pv_abs_sum_kvar | P_storage_L1_kW | P_storage_L2_kW | P_storage_L3_kW | P_storage_total_kW | Q_loss_total_kvar | Q_pv_total_kvar | P_pv_total_kW | Q_storage_total_kvar | Fcelu_2_A | objective_profile | J_used_total | J_used_component_1 | J_used_component_2 | J_used_component_3 | J_used_component_4 | J_used_component_5 | constraint_violations
1.0595 | 0.99157 | 0.032329 | 0.059548 | 0.036062 | 0.024853 | 0.033993 | 2.1624 | 0.0040936 | 0.012673 | 0.017368 | 0.021624 | 0.012623 | 70.7638 | 111.4729 | 119.0563 | 29.5399 | 9.1494 | 5.7027 | 3.4844 | 13.3637 | 22.5507 | 0 | 5.4404 | 36.3653 | 9 | 3 | 12 | 24 | 1.687 | -36.3653 | 142 | 0 | 9.1494 | critical_voltage |  | local_voltage_tracking | voltage_asymmetry_reduction | implicit_voltage_limits